##### APPLICATION:	ROOFING

##### ASSEMBLY:		EXTENSIVE GARDEN ROOF

##### W/FABRIC REINFORCED

MM 6125 (215 MILS)

EXTENSIVE GARDEN ROOF® ASSEMBLY

USING INSTAGREEN® GT-4 PRE-VEGETATED MODULES

LONG FORM SPECIFICATION

Note to Specifier:  This Guidespec is suitable for continental US projects; for projects located in Alaska, Hawaii and Puerto Rico, please contact Hydrotech for assistance.

PART I GENERAL

1.01	SUMMARY

A.	This specification serves as a guideline and shall be adapted to suit the needs of each individual project by the architect.  It is prepared in accordance with the CSI three-part section format and shall be included as a separate section under DIVISION 7 - Thermal and Moisture Protection.  Improvements and other changes to the contents shall be made only with the written approval of the architect.

1.02	RELATED SECTIONS (Note to Specifier: Edit to project requirements including Division numbering system in use for this project)

- DIVISION 2 - Sitework [Section 02500/02870] - Paving/Site Furnishings as supplied by American Hydrotech, Inc.  See Division 7 for specific details.

- DIVISION 3 - Concrete [Section 03300] - Roof Deck Surface/Substrate

The coordination of this section is necessary to facilitate the successful installation of the waterproofing membrane.

Cast in Place Concrete/Composite Deck

1.	Strength/density:  	minimum  2,500 psi (17,235 kPa) compressive strength

minimum 115 pcf (1842 kg/m3) density

2.	Finish:			Broom finish or equivalent similar to ICRI CSP 3 to 5.  Steel

troweled finish is not desirable.

3.	Concrete Hydration (Cure):

a.	Method of Cure:  Water cure, wet coverings, paper sheets, plastic sheets or approved liquid curing compound (sodium silicate preferred).

b.	Duration of Cure/Dry:

i.	Structural Weight Concrete:  recommend 28 days, minimum 14 days, prior to application of the membrane.

ii.	Lightweight Structural Concrete:  recommend 60 days, minimum 28 days, prior to application of membrane. Venting of the deck from the underside is recommended to facilitate drying.

iii.	The above minimum cure/dry times are recommended based upon basic concrete fundamentals and experience. Depending on conditions (i.e., ambient temperature, humidity) the concrete may be dry enough to receive application of the membrane in less than the 14 day minimum recommendation. Consult Hydrotech for specifics when less than the minimum is desired.

*REFER TO SECTION 3.02 PREPARATION FOR ADDITIONAL DECK TYPES.*

- DIVISION  [ ] - Wood blocking and curbing

- DIVISION  [ ] – Insulation

- DIVISION  [ ] - Sheet metal flashing and counterflashing

- DIVISION  [ ] - Prefabricated roof specialties

- DIVISION  [ ] - Caulking and sealants

- DIVISION  [ ] - Plumbing specialties

- DIVISION  [ ] - Roof hatches

- DIVISION  [ ] - Landscaping

1.03	REFERENCES

- American Society for Testing and Materials (ASTM).

- Canadian General Standards Board, CGSB-37.50-M89, Standard for Asphalt, Rubberized, Hot Applied, for Roofing and Waterproofing.

- Underwriters Laboratories (UL) Class A.

- ANSI/SPRI VR-1 2011 “Procedure for Investigating Resistance to Root Penetration on Vegetative Roofs”.

- International Concrete Repair Institute (ICRI) Concrete Surface Profile (CSP) Scale.

1.04 	DEFINITIONS

A.	Green Roof – An area of planting/landscaping, built up on a waterproofed substrate at any level that is separated from the natural ground by a man-made structure.

B.	Extensive Green Roof – Low maintenance landscaping consisting of shallow growing media depths (< 6 inches (152mm)) with plant varieties restricted to primarily mosses, herbs and succulents capable of withstanding harsh growing conditions.

- Intensive Green Roof – Landscaping requiring regular maintenance, consisting of deeper growing media depths (> 6 inches (152mm)) with a wider variety of plant species possible including shrubs and small trees.

- Lawn Green Roof – Lawn oriented landscaping requiring at-grade lawn oriented maintenance.  Can include sodded or seeded turfgrasses or naturalized grasses with growing media depths > 8 inches (203mm).

E.	Garden Roof® – Patented system of drainage, water retention and root barrier components utilized in the construction of green roofs over Hydrotech's MM 6125® roofing membrane.

F.	Steep Slope Green Roof – Defined as a slope exceeding 3:12 pitch.

- “C” Factor – The runoff coefficient used in the Rational Method, “C” represents the portion of the storm rainfall that becomes runoff.

- Curve Number (CN) – A number that is used with Natural Resource Conservation Service (SCS) methods to convert rainfall depth into runoff volume. The Curve Number takes into account a site’s soil type, plant cover, impervious cover, interception and surface storage.

1.05	SYSTEM DESCRIPTION

A.	Furnish and install a completed Extensive Garden Roof® Assembly including roof substrate board (if required), surface conditioner (if required), Monolithic Membrane 6125®-FR and flashings, protection course, root barrier protection, Styrofoam™ brand insulation (if required), filter fabrics of the types required, and pre-vegetated InstaGreen GT-4 modules.

B.	Irrigation (specified elsewhere) shall be coordinated during the installation of the pre-vegetated modules.

1.06	SUBMITTALS

- Certification from an approved independent testing laboratory experienced in testing rubberized asphalt material, that the material meets the CGSB-37.50-M89 standard for rubberized asphalt membranes, including applicable ASTM procedures.

- Certification that the roofing membrane has current validation by Underwriters Laboratories, or other approved independent validation service provider, of a minimum 40% recycled content (post-consumer).

- Certification that the roof membrane assembly is currently Class A listed with Underwriters Laboratories.

D.	Certification showing full time quality control of production facilities responsible for the manufacture of the rubberized asphalt and that each batch of material is tested to insure conformance with the manufacturers published physical properties.

E. 	Certification that the plant manufacturing the rubberized asphalt material has IS0 9001-2015 approval as evidenced by a copy of the official certificate.

F.	Certification showing that all components of the green roof assembly are being supplied and warranted by a single-source manufacturer.

- Certification that the extruded polystyrene insulation if used is free from CFC's.

- Ballasting requirements for the specified loose laid extruded polystyrene insulation, and as referenced in part 1.09.K., shall be provided to include the following:

1.	A written ballast review on membrane manufacturer’s letterhead outlining specific roof level ballasting requirements required to satisfy limited wind resistance warranty conditions.

2.	Each roof level shall be individually evaluated and prepared during the design and prebid process

3.	A final ballast review shall be submitted that reflects the designed conditions at the time of the project bid.

- Product data on all components of the green roof assembly shall be provided.

- Stormwater performance of the specific green roof assembly for the project shall be provided and include: (Note to Specifier: insert ## specific to given project)

- Total volume of water stored in the growing media shall be a minimum of ## cubic feet.

- Total volume of water stored in the water retention/drainage element shall be ## cubic feet.

- Evidence indicating that water is available at the roof level to ensure that the vegetation can receive sufficient moisture through proper maintenance of the green roof.

- Evidence that a contract is in place to maintain the vegetation to Hydrotech requirements once installed and throughout the warranty period.

- Certification from an approved independent testing laboratory that the vegetated tray assembly for use on the roof has been tested in accordance with CAN/CSA-A123.24-15 – “Standard Test Method for Wind Resistance of Modular Vegetated Roof Assembly” to a minimum wind speed of not less than 110mph without failure of the assembly.

1.07	QUALITY ASSURANCE

- The Roofing/Waterproofing Contractor shall demonstrate qualifications to perform the work of this Section by submitting the following documentation:

1.	Certification or license by the membrane manufacturer as a locally based, authorized applicator of the product the installer intends to use, for a minimum of five (5) years.

2.	List of at least three (3) projects, satisfactorily completed within the past five (5) years, of similar scope and complexity to this project.  Previous experience submittal shall correspond to specific membrane system proposed for use by applicator.

- The Green Roof Installing Contractor shall demonstrate qualifications to perform the work of this Section by submitting the following documentation:

- Certification or license by the green roof assembly supplier as a locally based, authorized applicator of the products the installer intends to use, for a minimum of five (5) years.

2.	List of at least three (3) projects, satisfactorily completed within the past five (5) years, of similar scope and complexity to this project.  Previous experience submittal shall correspond to specific membrane system proposed for use by applicator.

- The Green Roof Maintenance Contractor shall demonstrate qualifications to perform the work of this Section by submitting the following documentation:

- List of at least three (3) green roof projects, satisfactorily completed within the past five (5) years, of similar scope and complexity to this project.  Previous experience submittal shall correspond to specific membrane system proposed for use by applicator.

- Refer to Section 1.05 SYSTEM DESCRIPTION.  Include single-source for all components from the manufacturer.

- The rubberized asphalt membrane product shall contain an inert filler and crumb rubber to enable the product to be resistant to acids (fertilizers, building washes and acid rain) and maintain membrane thickness during application respectively.

- Membrane Manufacturer shall have available an in-house technical staff to assist the contractor, when necessary, in application of the products and final inspection of the assembly.

- Membrane Manufacturer Qualifications:  Manufacturer shall demonstrate qualifications to supply materials of this section by certifying the following:

1.	Membrane Manufacturer shall show evidence that the specified rubberized asphalt has been manufactured by the same source for thirty five (35) years and successfully installed on a yearly basis for a minimum of thirty five (35) years on projects of similar scope and complexity.

- Membrane Manufacturer shall not issue warranties for terms longer than they have been manufacturing their hot fluid rubberized asphalt membrane.

- Green Roof Supplier shall show evidence that the specified green roof assembly has been developed, marketed, supported and installed for a minimum of fifteen (15) years on projects of similar complexity.

- Green roof supplier shall provide data and calculations, specific to the products being submitted, that verify that the green roof assembly specified meets the project’s criteria for storm water runoff volume and rate control.

1.	Calculations shall be based on actual testing of supplier’s green roof components to be used for the project including but not limited to the regionally specific growing media formulation and water retention/drainage materials.

2.	Calculations shall account for vegetated and un-vegetated portions of the roof as well as local climatic conditions including rainfall depth, intensity, duration, and timing.

- Green roof supplier shall provide data demonstrating that the composite C-factor and Curve Number parameters for the specified green roof assembly are less than or equal to those factors used in the engineering design and analysis for the project’s drainage and storm water systems analysis.

K.	Pre-Construction Conferences.  The manufacturer will meet with the necessary parties at the jobsite to review and discuss project conditions as it relates to the integrity of the roofing assembly.

1.08	DELIVERY, STORAGE AND HANDLING

A.	Deliver materials in original unopened containers of packaging clearly labeled with manufacturer's name, brand name, instruction for use, all identifying numbers, and U.L. labels.

B.	Materials shall be stored in a neat, safe manner, not to exceed the allowable structural capacity of the storage area.

C.	Store materials in a clean, dry area protected from water and direct sunlight.

D.	Store all adhesives at temperatures between 60°F (15.5°C) and 80°F (26.6°C).  If exposed to lower temperatures, restore materials to 60°F (15.5°C) minimum temperature before using.

- Keep roof substrate board dry before, during, and after installation. Outside storage shall be off ground and protected by a breathable waterproof covering. Roof substrate board shall be roofed the same day as installed.

- Vegetation shall be handled and stored in accordance with the Hydrotech Extensive Garden Roof Plant Installation and Maintenance Guideline.

1.09	PROJECT CONDITIONS

- Application of the membrane shall not commence nor proceed during inclement weather.  All surfaces to receive the membrane shall be free of water, dew, frost, snow and ice.

- Application of membrane shall not commence nor proceed when the ambient temperature is below 0°F (-17.7°C).

- Preparation and application of membrane shall be conducted in well ventilated areas.

- Over its service life, do not expose membrane or accessories to a constant temperature in excess of 180°F (82°C) (i.e., hot pipes and vents or direct steam venting, etc.).

- Adhesives contain petroleum distillates and are extremely flammable.  Do not breathe vapors or use near an open fire.  Do not use in confined areas without adequate ventilation.  Consult container or packaging labels and Material Safety Data Sheets (MSDS) for specific safety information.

- Do not allow waste products (petroleum, grease, oil, solvents, vegetable or mineral oil, animal fat, etc.) to come in contact with the roof membrane.  Any exposure to foreign materials or chemical discharges shall be presented to membrane manufacturer for evaluation to determine any impact on the roof membrane assembly performance.

- Concrete Deck Surface Condition.  IMPORTANT- Refer to 1.02 RELATED SECTIONS.

- Deck Preparation; refer to Section 3.02 Preparation.

- Deck slopes greater than 3 inches in 12 inches (approx. 15 degrees or 25%) require special installation considerations.  CONTACT Hydrotech for specifics.

- The project design professional shall design the roofing/waterproofing assembly to properly locate the dew point condition and determine the need and location for a vapor retarder to prevent excessive condensation contamination within the roofing/waterproofing assembly and/or delamination of the roofing/waterproofing membrane from the substrate.

- The project design professional shall design the roofing/waterproofing assembly to remain in place withstanding the wind speeds and uplift pressures as determined for the roof sections of the project.

- General Contractor shall assure that adequate protection is to the membrane and plantings to prevent damage from subsequent trade traffic.

1.10	WARRANTY

A.	Upon completion of the work, the contractor shall supply the owner with a single-source warranty of U.S. origin direct from the manufacturer.

B.	Each warranty varies in scope and terms.  CONTACT Hydrotech for exact warranty terms and conditions to meet the specific project requirements.

C.	Warranties available from the manufacturer: (Note to Specifier: Edit to project requirements)

1.	Material Warranty; excludes labor.

Duration:  2-, 5-, 10-, 20-year (Note to Specifier: Edit to required duration)

2.	Watertightness Warranty; includes labor and material to maintain watertight condition and replacement of Hydrotech supplied roof substrate board.

Duration:  5-, 10-, 15-, 20-year (Note to Specifier: Edit to required duration)

- Thermal Warranties; includes 90% retention of the original thermal value

Duration 5-, 10-, 15-, 20-year

Note to specifier: A limited wind resistance warranty, may also be available for the insulation.  Contact Hydrotech DURING THE DESIGN PHASE for project specific ballasting assistance or guidelines.

4.	Total System Warranties; covers components of the green roof assembly, including membrane, flashing, insulation, Garden Roof® components, InstaGreen® GT-4 modules and vegetation, pavers and Checker Block ballast units. Includes removal and reinstallation of the insulation, Garden Roof® components, vegetation, pavers, and InstaGreen® GT-4 modules when supplied, installed, and maintained per Hydrotech's requirements, and replacement of Hydrotech supplied roof substrate board.

- Duration of Membrane/Flashing and replacement of Hydrotech supplied roof substrate board from date of installation (watertight condition):

- 5-, 10-, 15-, 20-year (Note to Specifier: Edit to required duration)

- Duration of Insulation from date of purchase:

- 5-, 10-, 15-, 20-year (Note to Specifier: Edit to required duration)

  - 90% of original thermal value

Note to specifier: A limited wind resistance warranty, may also be available for the insulation.  Contact Hydrotech DURING THE DESIGN PHASE for project specific ballasting assistance or guidelines.

- Material Integrity of Garden Roof® Components from date of purchase:  5-, 10-, 15-, 20-year (Note to Specifier: Edit to required duration)

- InstaGreen GT-4 module (components only):  1-year from date of installation.

- Extensive Vegetation: 2-year thrive and coverage from date of installation:

- InstaGreen® GT-4 Module: 75% coverage at delivery and end of year 1; 90% coverage end of year 2

- Duration of Pavers from date of purchase: 5-, 10-year (will not crack, split or delaminate due to freeze-thaw)

**CONTACT HYDROTECH FOR EXACT WARRANTY TERMS AND CONDITIONS.**

PART II PRODUCTS

2.01	GENERAL

A.	Refer to Section 1.05   SYSTEM DESCRIPTION.  All components shall be obtained as a single-source from the membrane / green roof manufacturer to ensure total system compatibility and integrity.

Manufacturer:		American Hydrotech, Inc.

401 N. Michigan Ave, Suite 1550

Chicago, Illinois 60611

800-877-6125 or 312-337-4998

Web Site:  www.hydrotechusa.com

2.02	MATERIALS

A.	Membrane

1.	Membrane shall be a hot, fluid applied, rubberized asphalt membrane meeting the CGSB-37.50-M89 standard and other pertinent physical properties:

- American Hydrotech, Inc., Monolithic Membrane 6125®

(40% post-consumer recycled content)

| PROPERTY | TEST METHOD | - REQUIREMENT |
| --- | --- | --- |
| Flash point | CGSB-37.50-M89 ASTM D-92 | > 500°F* (260°C) |
| Penetration | CGSB-37.50-M89 ASTM D-5329 | @ 77°F (25°C) max. 110 @ 122°F (50°C) max. 200 |
| Flow | CGSB-37.50-M89 ASTM D-5329 | @ 140°F (60°C) max. 3.0mm |
| Toughness | CGSB-37.50-M89 | ≥ 5.5 Joules |
| Ratio of Toughness to Peak Load | CGSB-37.50-M89 | ≥ 0.040 |
| Water Vapor Permeability | CGSB-37.50-M89 ASTM E-96, Procedure E | ≤ 1.7 ng/Pa.s.m2 (0.027 perm) |
| Water Absorption | CGSB-37.50-M89 | Gain in weight 0.35 g max. Loss in weight 0.18 g max. |
| Low Temperature Flexibility (-25°C) | CGSB-37.50-M89 | No delamination, adhesion loss, or cracking |
| Low Temperature Crack Bridging Capability | CGSB-37.50-M89 | No cracking, adhesion loss, or splitting |
| Heat Stability | CGSB-37.50-M89 | No change in viscosity, penetration, flow or low temperature flexibility |
| Viscosity | CGSB-37.50-M89 | 2 - 15 seconds |
| Water Resistance (5 days/50°C) | CGSB-37.50-M89 | No delamination, blistering, emulsification, or deterioration |
| Softening Point | ASTM D-36 | 180°F (82°C) |
| Elongation | ASTM D-5329 | 1000% minimum |
| Resiliency | ASTM D-5329 | 40% minimum |
| Bond to Concrete 0°F (-18°C) | ASTM D-5329 | Pass |
| Resistance to Acid | ASTM D-896 Procedure 7.1 (N-8) | Pass - 50% Nitric Acid Pass - 50% Sulfuric Acid |
| Resistance to Hydrostatic Pressure | ASTM D-08.22 Draft 2 | 100 psi (equals 231 foot of head water) |
| Resistance to Salt Water (20% Sodium carbonate calcium chloride) | ASTM D-896 similar | No delamination, blistering, emulsification or deterioration |
| Resistance to Fertilizer (Undiluted 15/5/5, nitrogen/phosphorus/potash) | ASTM D-896 similar | No delamination, blistering, emulsification or deterioration |
| Resistance to Animal Waste | 3-year exposure | No deterioration |
| Solids Content |  | 100% - no solvents |
| Recycled Content | UL Validated | 40% (post-consumer) (30% REACH compliant) |
| Shelf Life |  | 10 years (sealed) |
| Specific Gravity |  | 1.15 + .02 |
| * Or alternatively not less than 25oC above the manufacturer’s maximum recommended application temperature |  |  |

- Roof Substrate Board (if required) (Note to Specifier: Edit to project requirements)

1.	Impact resistant, nonstructural, fiber-reinforced, gypsum panels made from 95% recycled content.

- Securock Gypsum-Fiber Roof Board as marketed by American Hydrotech, Inc.

  - Miscellaneous

    - Fasteners and Plates

Provide size and type in accordance with Factory Mutual and/or applicable codes and to maintain structural integrity. Only 3 inch round metal plates shall be used.

    - Adhesive

Provide adhesive compatible with roof substrate board and insulation to

comply with Factory Mutual and/or applicable codes and to maintain

structural integrity.

    - Vapor Barrier

Provide suitable vapor retarder as required by design professional.

2.	Other approved fire rated type "X" gypsum roof substrate board.

- Surface Conditioner

1.	Asphaltic surface conditioner for concrete surfaces only

- American Hydrotech, Inc., Surface Conditioner

- Reinforcing

1.	Spunbonded polyester fabric (standard duty) reinforcing sheet.

- American Hydrotech, Inc., Flex Flash® F

2.	60-mil (1.5 mm) thick, uncured neoprene (heavy duty) reinforcing sheet.

- American Hydrotech, Inc., Flex Flash® UN

- Flashing (Note to Specifier: Edit to project requirements)

1.	60-mil (1.5 mm) thick, uncured neoprene sheet.

- American Hydrotech, Inc., Flex Flash® UN

2.	157-mil (4 mm) thick, torch-grade, modified asphalt, reinforced flashing membrane.

- American Hydrotech, Inc., Flex-Flash® MB

- Two-component, liquid applied resin membrane flashing system.

- American Hydrotech, Inc., HydroSeal Resin

- poly methyl-methacrylate (PMMA) resin

- American Hydrotech, Inc., HydroSeal Matrix

- acrylic resin with integral chopped polymer fiber reinforcement

- American Hydrotech, Inc., HydroSeal Flashing Accessories

- resin based primers, additives, reinforcing fleece, surfacing topcoats

- One-component, liquid applied membrane flashing system

  - American Hydrotech, Inc., HydroSeal 1K PU – Membrane

- Aliphatic and alkaline resistant, low VOC polyurethane (PU) resin

  - American Hydrotech, Inc., HydroSeal 1K accessories

- Epoxy based primer, fiber reinforcement, fleece

(Note to Specifier: CONSULT Hydrotech for recommended products

and uses.)

- Adhesives/Sealant

1.	Contact adhesive to bond elastomeric flashing together.

- American Hydrotech, Inc., Splicing Cement

2.	Contact adhesive to bond elastomeric flashing to an approved substrate.

- American Hydrotech, Inc., Bonding Adhesive

3.	Sealant to seal elastomeric flashing seam edge.

- American Hydrotech, Inc., Lap Sealant

4.	Tape to bond laps of uncured neoprene flashings

- American Hydrotech, Inc., Seam Tape

- Separation/Root Barrier Protection Course

1.	Combination of a fiberglass reinforced rubberized asphalt protection sheet and polyethylene root barrier.

- American Hydrotech, Inc., Hydroflex® 30 and Root Stop

2.	Pressure-sensitive polyethylene tape for Rootstop and Rootstop HD

- American Hydrotech, Inc. Root Stop Tape

- Prefabricated Drainage Course (Note to Specifier:  If required, consult Hydrotech)

1.	Composite drainage system consisting of a three-dimensional, crush-proof, drainage core and a filter fabric.

- American Hydrotech, Inc., Hydrodrain® 300

- Insulation (Note to Specifier: Edit to project requirements)

1.	Extruded polystyrene rigid board insulation for use above membrane.

- Styrofoam™ brand insulation [TYPE] as manufactured by DuPont™, marketed by American Hydrotech, Inc.

a.	Insulation shall meet ASTM C-578, Type VI or VII.

b.	Minimum compressive strength, ASTM D-1621, 40 or 60 psi (276 or 414 kPa) (variance by type of product)

c.	Maximum water absorption by volume per ASTM C-272, 0.3%

d.	Water vapor permeance for 1" product per ASTM E-96, 0.8 perm (max.) (63 ng/Pa/s/m2)

e.	Insulation shall have an R value of 5.0°F ft2 h/Btu/in. (0.88 K m2/W) of thickness when tested at 75°F (23.9°C) mean temperature in accordance with ASTM C-518

f.	Product shall be free of CFC's

Product types available:  Styrofoam™ brand, RoofMate; Ribbed RoofMate; PlazaMate; and High Load 100. (Note to Specifier: CONSULT Hydrotech for recommended product type.)

- Extruded polystyrene rigid board insulation for use as flat fill and tapered insulation below roof substrate board.

- Styrofoam™ brand insulation [TYPE] as manufactured by DuPont™, marketed by American Hydrotech, Inc.

a.	Insulation shall meet ASTM C-578, Type IV.

b.	Minimum compressive strength, ASTM D-1621, 25 psi (172.4 kPa)

c.	Maximum water absorption by volume per ASTM D-2842, 0.7%

d.	Water vapor permeance for 1" product per ASTM E-96, 1.1 perm (max.) (63 ng/Pa/s/m2)

e.	Insulation shall have an R value of 5.0°F ft2 h/Btu/in. (0.88 K m2/W) of thickness when tested at 75°F (23.9°C) mean temperature in accordance with ASTM C-518

f.	Product shall be free of CFC's

Product types available:  Styrofoam™ Brand, DeckMate Plus, DeckMate Plus FA, Tapered DeckMate Plus FA. (Note to Specifier: CONSULT Hydrotech for recommended product type.)

- Filter Fabric

- Non-woven, polymeric, geotextile fabric.

- American Hydrotech, Inc., Systemfilter (for use as indicated on details and with cut InstaGreen® GT-4 modules)

- Vegetated Module (Note to Specifier:  Edit to project requirements, consult Hydrotech)

- InstaGreen® GT-4 module as marketed by American Hydrotech with the following characteristics:

| - Description: | - Three-dimensional unit integrating a moisture retention/drainage base, perforated sidewalls with locking clips, engineered growing media, and vegetation designed to form an integrated module for use within the Hydrotech Garden Roof® Assembly. |
| --- | --- |
| - Dimensions: | - 12” x 24” (2.0 SF per module) - 4” sidewalls - 5¾” total height |
| - Walls: | - Perforated walls and reinforcing ribs (total width approximately ½”) |
| - Maximum Weight: | - 32 lbs. per SF, saturated (may vary due to local media composition) |
| - Moisture Holding Capacity: | - 2.9 gallons per units (may vary due to local media composition) |
| - Materials: | - 100% Recycled High Density Polypropylene Empty Module - 100% Recycled Non-woven filter fabric - Engineered growing media designed for optimum plant growth |
| - Plant Materials | - Standard sedum blend is available (contact Hydrotech for details) - Can be planted with perennial blends (contact Hydrotech for details) |
| - Irrigation | - InstaGreen® GT-4 module can be fitted with integral popup irrigation components (specified and supplied by others). |

- Stone Filter Fabric

1.	Water permeable polymeric fabric.

-American Hydrotech, Inc., Stone Filter Fabric (for use under stone ballast and InstaGreen® GT-4 modules

- Hardscape / Roof Ballast (Note to specifier: Edit to project requirements)

1.	Pavers

a.	Ballast Pavers

- American Hydrotech, Inc., Ballast Pavers, meeting the following physical properties:

| PROPERTY | TEST METHOD | VALUES |
| --- | --- | --- |
| Compressive Strength | ASTM C140 | >7,000 psi average min. |
| Flexural Strength | ASTM C293 | >600 psi average min. |
| Water Absorption | ASTM C140 | Not greater than 5% |
| Freeze/Thaw | ASTM C67 | <1% loss/dry weight (50 cycles) |
| Centerload | - | Min. 1,750 lbs. |

b.	Architectural Finish Pavers

- American Hydrotech, Inc., Architectural Pavers, meeting the following physical properties:

| PROPERTY | TEST METHOD | VALUES |
| --- | --- | --- |
| Compressive Strength | ASTM C140 | >7,000 psi average min. |
| Flexural Strength | ASTM C293 | >600 psi average min. |
| Water Absorption | ASTM C140 | Not greater than 5% |
| Freeze/Thaw | ASTM C67 | <1% loss/dry weight (50 Cycles) |
| Centerload | - | Min. 1,750 lbs. |

2.	Stone Ballast

Well screened and washed stone gravel meeting ASTM D-448-80, gradations #2, #4 or #5 as directed by DuPont™ and American Hydrotech, Inc.

3.	Concrete Pour Topping

(Note to specifier: DuPont™, manufacturers of Styrofoam™ brand insulation, recommends the incorporation of an air layer between the insulation and concrete.  Hydrotech suggests the use of Hydrodrain AL for this purpose.)

- Miscellaneous

- Metal Edging

Aluminum edging perforated to allow water flow as shown on plans and details.

- 	American Hydrotech, Inc. GardenEdge® Metal Edge Restraint; size as noted on plans and details.

-	American Hydrotech, Inc. GardenEdge® Aluminum Leveling Strips:  available to accommodate sloped/level roof surfaces.

(Note to Specifier:  please indicate size and finish of GardenEdge® metal edging and any leveling strips needed on plans and details.  Mill finish aluminum is standard.  Color coatings and other metals are available including stainless steel and Cor-Ten weathering steel; contact Hydrotech for further details.)

- Inspection Chambers

Aluminum and stainless steel over drain chambers perforated to allow water flow as shown on plans and details.

- 	American Hydrotech, Inc. GardenHatch® Inspection Chambers; size as noted on plans and details.

(Note to Specifier:  please indicate size of GardenHatch® inspection chambers on plans. Custom sizes are available; contact Hydrotech for further details.)

- Prefabricated Concrete Curbing

High density, hydraulically pressed, prefabricated concrete curbing units as shown on plans and details.

- 	Hanover Architectural Products Rock Curb® as marketed by American Hydrotech, Inc. size as noted on plans and details.

(Note to Specifier:  Per standard product line:  please indicate configuration, layout, size, color and edge profile of Rock Curb® on plans and details)

2.03 	RELATED MATERIALS

- Metal counterflashing is typically required to provide protection to vulnerable flashing materials from damage due to gardening activities.

PART III EXECUTION

3.01	INSPECTION

A.	The roofing contractor shall examine all surfaces to receive the roofing assembly to verify it is acceptable and proper for the application of the membrane.  Refer to American Hydrotech's Pre-Installation & Application Guidelines.

B.	The roofing contractor shall not proceed with the installation of the roof membrane assembly until all roof defects have been corrected.

3.02	PREPARATION

A.	All surfaces shall be dry, smooth, free of depressions, voids, protrusions, clean and free of unapproved curing compounds, form release agents and other surface contaminants. (Edit to project requirements)

(Note to Specifier: Edit to project requirements)

1.	Cast in-place concrete/Composite deck

a.	Poured in place concrete shall be monolithic, smooth, free of voids, spalled areas, laitance, honeycombs, and sharp protrusions.

b.	Refer to Section 1.02 of this specification, Division 3.

2.	Precast concrete decks

- Precast units shall be mechanically secured to minimize differential movement and all joints between units shall be grouted or caulked.

- Joints shall be pre-detailed with membrane and the appropriate manufacturer required reinforcing prior to full membrane application.

- Plywood decks

- Minimum thickness of 1/2" (12.7 mm) is required with adequate structural support.

- Tongue and groove joint edges are required.

- Adequate number and type of fasteners shall be used to comply with applicable codes and maintain structural integrity.

4.	Metal Deck with roof substrate board

a.	Roof substrate board board shall be fire rated type "X" board attached to minimum 22 gauge steel decking with adequate structural support.

- Minimum 5/8 inch thick substrate board shall be used directly to metal deck.

- Minimum 1/2 inch thick substrate board shall be used over insulation.

- Flat fill and tapered roof insulation shall be installed in accordance with layout indicated on shop drawings and insulation board manufacturer’s minimum requirements.

- Adequate number and type of fasteners and plates shall be used to comply with roof substrate and insulation board manufacturer’s minimum requirements and applicable codes and to maintain structural integrity.

- Minimum of 10 fasteners and plates per full-size roof board shall be used.

- Appropriate roof adhesive shall be used in accordance with adhesive manufacturer requirements to comply with applicable codes and maintain structural integrity.

- Size and spacing of adhesive beads shall be as required by adhesive manufacturer.

- Roof substrate boards shall be installed such that all edge and end joints are supported by metal deck ribs and/or appropriate blocking.

- Roof substrate board end joints of adjacent lengths shall be staggered.

- Where required, a suitable vapor barrier membrane shall be applied as determined by the project design professional prior to installation of the roof substrate board and/or insulation.

- Roof substrate board edges and ends shall be butt loosely in typical installations. Long, uninterrupted runs (greater than 200 feet) of roof substrate board may require slight gapping due to higher temperature gain. Gapping shall not exceed 3/16 inch and all such gaps shall be filled flush with the surface of the roof board with an appropriate sealant. CONTACT Hydrotech for specifics.

- Roof substrate board shall be cut to size using a sharp utility knife and straightedge. The surface of the roof substrate board shall be scored with the utility knife and the board bent up sharply towards the score cut. A keyhole-type drywall saw shall be used for penetration cutouts and radii. A low rpm circular saw shall be used for 5/8 inch thick roof board.

- Re-Roof/Tear-Off Application

- Asphalt, coal tar pitch or other existing membrane shall be removed.  CONTACT Hydrotech.

- Deck type acceptable to Hydrotech.

B.	Substrate cleaning

1.	Thoroughly sweep the substrate which is to receive the roof membrane.

2.	Substrate shall also be blown clean using an air compressor to remove any remaining loose debris.

3.	Final check to determine if concrete has been properly cleaned is to apply a test patch of Monolithic Membrane 6125 to the surface and check its adhesion.

3.03	INSTALLATION

A.	Surface conditioner application (to concrete substrates only)

1.	Apply the surface conditioner only to concrete using a hand held sprayer evenly at a rate of 300 to 600 SF/gallon (7.4 - 14.7 m2/L) depending on surface texture.  Surface conditioner shall "tan" the surface, not blacken it.

2.	Allow sufficient time for the surface conditioner to thoroughly dry prior to the membrane application.

B.	Membrane preparation

1.	The membrane shall be heated in double jacketed, oil bath or hot air melter with mechanical agitation, specifically designed for the preparation of a rubberized asphalt membrane.

2.	Heat membrane until membrane can be drawn-free flowing at a temperature range between 350°F (176°C) and 375°F (190°C).

C.	Detailing/Flashing

1.	All detailing and flashing shall be done in accordance with the manufacturer's standard guideline details.

2.	All detailing and flashing shall be completed before installing the membrane over the field of the substrate.

3.	Roof substrate board joints shall be pre-detailed with membrane and fabric reinforcing prior to full fabric reinforced membrane application.

- All liquid-applied, resin flashings shall be applied over properly completed membrane flashing details in accordance with the manufacturer’s standard guideline details.

D.	Membrane Application

1.	Apply the rubberized asphalt membrane at a rate to provide a continuous, monolithic coat of 90 mil minimum (approximately 2.3 mm), into which is fully embedded a layer of the spunbonded polyester fabric reinforcing sheet, followed by another continuous monolithic coat of membrane at an average thickness of 125 mil (approx. 3.2 mm).  Total membrane thickness is to be 215 mils average (approx. 5.5 mm), 180 mils minimum.

2.	Overlap fabric reinforcing sheet 1-2 inches (25.4 mm - 50.8 mm) with membrane between sheets.

- Pre-detailing of joints between plywood and roof substrate board decks is required.

3.04	SEPARATION/PROTECTION COURSE INSTALLATION

A.	Separation/Protection course shall be installed as follows:

- Embed the Hydroflex 30 separation/protection course into the membrane while it is still hot to insure a good bond. Installation of a separation course is necessary in order to carry out the water test.

- Overlap adjoining sheet edges (dry) a minimum of 2"-3" (50.8 mm - 76.2 mm) to insure complete coverage.

3.05	MEMBRANE INTEGRITY TEST

- The roof area or portions thereof shall be leak tested by means of Electronic Leak Detection (ELD) or by ponding water at a minimum depth of 2" (50.8 mm) for a period of 48 hours to check the integrity of the membrane installation.

  - ELD testing should be performed on all installed membrane assembly. Testing is to be performed in accordance with ASTM D7877 or ASTM D8231. Areas that are ELD tested should be covered immediately

  - VERIFY that the structure can support the deadload weight of a water test before testing.

  - If leaks should occur the water shall be drained completely and the membrane installation repaired.

- In the event of excessive damage to the membrane assembly, Electronic Leak Detection testing shall be required prior to the placement of subsequent overburden.

  - GARDEN ROOF COMPONENTS INSTALLATION

- All Garden Roof components shall be installed per Hydrotech’s requirements.

- Root Barrier Protection:  Root Stop shall be laid over the Hydroflex 30, lapping adjacent sheets 5 feet (1.5 m). A minimum 30 inch overlap is acceptable when Root Stop Tape is used to continuously seal the lap edge.  Root Stop shall be turned up all vertical roofed/flashed surfaces, installing additional material as required, to completely protect waterproofing and flashings.

- Insulation:  Where specified, Styrofoam™ brand insulation shall be installed loose-laid in accordance with manufacturer's recommendations.

- Filter Fabric:  Systemfilter shall be used to contain media in cut ends of InstaGreen GT-4 modules and when small pockets of media and vegetation are required to fill odd shaped spaces.  See Hydrotech details.

- InstaGreen GT-4 installation shall be as indicated below.

3.07	HARDSCAPE/ACCESSORY INSTALLATION

- Stone and/or paver ballast shall be installed at all roof perimeters, building walls, penetrations, and access hatches and as required for vegetation free zones, proper wind design, fire breaks, and as walkway/maintenance paths.

- Ballast design shall be in accordance with DuPont™ and American Hydrotech, Inc. requirements. CONTACT Hydrotech for ballasting recommendations.

- Metal edge restraints, precast curbing and all specified edging materials shall be installed as shown on plans and details and in accordance with manufacturer’s recommendations.

C.	Drains shall be fitted with inspection/maintenance chambers and grills, built up to ensure access at growing media level as shown on plans and details.

  - IRRIGATION (SPECIFIED IN OTHER SECTIONS)

A.	Integrate irrigation at same time as installation of InstaGreen GT-4 modules.  Coordinate irrigation supply lines and sprinkler heads or drip lines with modules prior to installation.

3.09	INSTAGREEN® GT-4 MODULE INSTALLATION

  - InstaGreen® GT-4 modules shall be installed in accordance with the Hydrotech Extensive Garden Roof Installation Guidelines.

  - Stone Filter Fabric shall be installed under InstaGreen® GT-4 modules.

  - Plant materials shall not be installed between the fall frost date and the following spring frost date.  Contact Hydrotech for fall and spring frost dates specific to the Project and plant material type.

  - All vegetation shall be thoroughly watered and saturated immediately after installation.  Media is saturated when water is seen flowing into roof drains from adjacent areas.

3.10	VEGETATION MAINTENANCE

- Contractor/Installer shall maintain plantings in accordance with the Hydrotech Extensive Garden Roof Maintenance Guidelines.  Contact Hydrotech for specific maintenance requirements.

- Maintenance activities shall include, but are not limited to, the following:

  - Periodic on-roof monitoring of vegetation

  - Watering to maintain proper growing media moisture content (especially during periods of hot and dry weather)

  - Weeding to remove unwanted vegetation from planted areas and vegetation free zones.

  - Removal of debris

  - Reporting and photo-documentation of progress of vegetation during maintenance and warranty period.

- Maintenance shall begin immediately after vegetation installation and shall continue through final acceptance and turn-over of the project to the owner.

- Maintenance activities shall continue throughout the two-year warranty period (from date of vegetation installation) to keep vegetation warranty referenced above under Paragraph 1.10 WARRANTY in effect.

#### END OF SECTION